## Slide 1: CMU Hackathon Power System Dynamics
Steve Abate, Gian Alian
September 2020

## Slide 2: DLC Hackathon Team
Steve Abate
Transmission Planning Engineer
Hackathon Mentor
Gian Alian
Transmission Planning Engineer
Hackathon Mentor
Elizabeth Cook
Senior Manager of Transmission and Distribution Planning
Hackathon Judge

## Slide 3: DLC Company Profile
Located in Pittsburgh, PA serving Allegheny & Beaver Counties
Approximately 600,000 customers
Service area ~705
2019 Metered Peak Load: 2640 MW

## Slide 4: Presentation Overview
DLC Transmission Planning
Power System Dynamics
Hackathon Challenges
Description of Dataset
Output Requirements

## Slide 5: Transmission Planning Assessment Overview
Generators
Transmission Network
Loads

## Slide 6: Transmission Planning Assessment Overview
Generator #1
100 MW
Load
300 MW
Generator #2
100 MW
Generator #3
100 MW
Steady-state analysis
Short-circuit analysis
Stability analysis
Although there are different types of studies, the goal of all transmission studies is to identify whether or not system limits are exceeded during normal and contingency conditions.

## Slide 7: Transmission Planning Assessment Overview
Generator #1
100 MW
Load
300 MW
Generator #2
100 MW
Generator #3
100 MW
X
Contingency:
Loss of Line A
Line B
105% of rating
Although there are different types of studies, the goal of all transmission studies is to identify whether or not system limits are exceeded during normal and contingency conditions.
Steady-state Analysis Example:
Can the system operate within limits after losing Transmission Line A?
Load Bus
0.941 per-unit voltage

## Slide 8: Transmission Planning Assessment Overview
Generator #1
100 MW
Load
300 MW
Generator #2
100 MW
Generator #3
100 MW
Fault on Line A
Although there are different types of studies, the goal of all transmission studies is to identify whether or not system limits are exceeded during normal and contingency conditions.
Short-circuit Example:
Can the system clear a fault on Transmission Line A?
59 kA
30 kA
59 kA fault current exceeds breaker interrupting capacity
50 kA

## Slide 9: Transmission Planning Assessment Overview
Generator #1
100 MW
Load
300 MW
Generator #2
100 MW
Generator #3
100 MW
Although there are different types of studies, the goal of all transmission studies is to identify whether or not system limits are exceeded during normal and contingency conditions.
Stability Example:
Can the system stabilize after the protection system clears a fault?
Fault on Line A
Line A cleared in
~8 cycles
Model Generator dynamics
Voltage response:
Unstable

## Slide 10: Transmission Planning Assessment Overview
Transmission System Analysis
  NERC Planning Criteria Compliance
  Load and Generator Deliverability
  N-1-1 Analysis
  Short Circuit
  Stability
  Light Load
  Winter Peak
  Generation Deactivation
More information on RTEP analysis can be found in PJM Manual 14B

## Slide 11: Power System Stability
What is power system stability?
  “Power system stability may be broadly defined as the property of a power system that enables it to remain in a state of operating equilibrium under normal conditions and to regain an acceptable state of equilibrium after being subjected to a disturbance”
Disturbances:
  Transmission System Faults
  Sudden Large Load Changes
  Loss of Generating Units
  Line Switching
  Etc.

## Slide 12: Power System Dynamic Model
Generators
Transmission Network
Loads

## Slide 13: Power System Dynamic Model
Overview
Generators
Transmission Network
Loads
1
n
Large Motor
Small Motor
1
2
m
Load Dynamics
Discharge Lighting
Transformer Saturation
Generator Dynamics

## Slide 14: Power System Dynamic Model
PJM MMWG Model
  Network Data
    ~80,000 buses
    ~74,000 transmission lines
    ~21,000 transformers
    ~9,000 generators
  Dynamic Data
    Machine Models
    (25+ parameters each)
      Exciter
      Governor
      Stabilizer
    Wind Generator Models (15+ parameters each)
    Load Models (~8 parameters each, but some have 130+ parameters each)
  Hundreds of contingencies for DLC assessment

## Slide 15: Simulation Results
System response to minor disturbance
(138 kV transmission line fault with normal clearing)
Voltage at DLC 138 kV bus after nearby 138 kV fault
Disturbance
At t=1 sec

## Slide 16: Simulation Results
System response to larger disturbance
(500 kV transmission line fault with delayed clearing)
Voltage at DLC 345 kV bus after
500 kV fault in other territory
Disturbance
At t=1 sec

## Slide 17: Hackathon Problem Statement
Problem – Current simulation data processing relies on manual methods to identify key parameters. Given the large amount of data produced by dynamic simulations, this can be time consuming.
Challenge – Develop a scripted method to perform a set of tasks on each simulation results file.

## Slide 18: Hackathon Challenge
Hackathon Challenge – Create a scripted method to perform the following tasks on power system dynamic simulation data.
Task #1 – Create graphic plot of power system variables
  Generator Terminal Voltage (ETRM), Generator Power (POWR), Generator Speed (SPD), Bus Voltages (VOLT)
Task #2 – Identify the time at which the disturbance occurs
  Power system variables will begin to fluctuate at the time of the disturbance
Task #3 – Identify whether or not the system remains stable
  The system is stable if all power system quantities in Task #1 reach a steady-state (constant) value after the power system event.
Task #4 – Do all voltages restore in accordance with PJM criteria?
  Calculate the recovery time for each bus voltage.
Task #5 – Does the system stabilize with sufficient damping per PJM criteria?
  Calculate the damping of the Generator Speed (SPD) for each generator
  Refer to the provided document “PSSE Documentation – Modal Analysis.pdf” for more information.

## Slide 19: Task #1: Create a graphic plot of power system variables – the plot should include axis labels, title, and legend

## Slide 20: Task #2: Identify the time at which the disturbance occurs – Power system disturbance will cause a large drop in voltage
Time at which disturbance occurs

## Slide 21: Task #3: Identify whether or not the system remains stable – Some power system disturbances cause machine variables (voltage, power, and speed) to go unstable
Note: Speed can appear non-oscillatory for an unstable case. However, notice how they lose synchronism and deviate from each other.
Stable System
Unstable System

## Slide 22: Task #4 & #5
PJM criteria for acceptable stability
(per PJM Manual 14B):
Recover to minimum of 0.7 p.u. after 2.5 seconds
Damping exceeds 3%

## Slide 23: Task #4 & #5
PJM criteria for acceptable stability
(per PJM Manual 14B):
Recover to minimum of 0.7 p.u. after 2.5 seconds
Damping exceeds 3%
0.7 p.u.
Recovery time:
How fast voltage recovers to 0.7 p.u.
“When a fault occurs on the transmission system, system voltages are temporarily reduced. Once the fault is cleared, voltages follow transient voltage recovery trajectories governed by system dynamics. […] the voltage following fault clearing shall recover to a minimum of 0.7 p.u. after 2.5 seconds.”
2.5 sec

## Slide 24: Task #4: Calculate the recovery time for each bus voltage
Amount of time it takes for the machine voltage to recover to 0.7 p.u.

## Slide 25: Task #5
PJM criteria for acceptable stability
(per PJM Manual 14B):
Recover to minimum of 0.7 p.u. after 2.5 seconds
Damping exceeds 3%
Damping: How fast
the system stabilizes
“A sustained oscillatory system response, even if slightly damped, will cause the system to be in a vulnerable state and exposed to adverse impacts for subsequent changes to the system over some prolonged time.”

## Slide 26: Task #5 – Modal Analysis
Modal Analysis
Goal of modal analysis is to represent the signal as a sum of decaying exponential sinusoids.
For the transient period (~5-10 seconds after event), non-linear characteristics can be dominant.
Normally, modal analysis is performed 10-15 seconds after the event (we recommend using 30-40 seconds for these events)
  Experiment with the selected window and compare the results.
Refer to the attachment “PSSE Documentation - Modal Analysis.pdf” for more information

## Slide 27: Task #5 – Modal Analysis
A – real part of dominant mode
B – imaginary part of dominate mode
In this example, the eigenvalue of the dominant mode is:

## Slide 28: Task #5 – Modal Analysis

## Slide 29: Task #5 – Modal Analysis
½
½
Once modal analysis is performed, the dominant mode can be used to approximate the signal.

## Slide 30: Task #5 – Modal Analysis
Note: The dominant mode can be also expressed in a cosine form.

## Slide 31: Description of Dataset
The challenge dataset is based on a simple eight (8) bus test system:
  Four (4) generators
  Two (2) shunt capacitors
  Two (2) loads
The dataset consists of dynamic simulation results for 369 different events.

## Slide 32: Description of Dataset
Example: Simulation # 96
Fault occurs at Bus 7

## Slide 33: Description of Dataset
Example: Simulation # 96
Protection system clears fault by
opening nearby branches
Protection system responds and
isolates the fault in ~9 cycles
(Note: One cycle is )

## Slide 34: Description of Dataset
Example: Simulation # 96

## Slide 35: Description of Dataset
Columns for each power system variable
The Hackathon dataset includes time-series power system quantities for each simulation (369 total)
0.csv
1.csv
2.csv
…
366.csv
367.csv
368.csv
369.csv
Comma-separate file
for each simulation:

## Slide 36: Output Requirements
For each simulation, the following information should be reported:
  Simulation number
  Plot of Power System Variables – Task #1
  Disturbance Time (s) – Task #2
  Stable (Yes / No) – Task #3
  Recovery Time (s) – Task #4
  Modal Analysis Results – Task #5
    Although the 30-40 sec window is recommended for this challenge, please investigate how the window selection will impact modal analysis results as the proper window is not always known.